Inspecting, Testing & Commissioning Workbook

| Name: |  | Group: |  |
| --- | --- | --- | --- |

The purpose of this workbook is to try to cover the Learning Outcomes found within the EAL Unit 06 syllabus and to get you to demonstrate an understanding of the requirements and procedures of inspecting, testing and commissioning electrical installation work.

References for study including Text Book B Chapter ELTK 06, BS7671:2018, the IET On-Site Guide and the IET Guidance Note 3 and YouTube video links, are shown below each answer box.

The term Inspection and Testing are often used interchangeably, however:

- the Inspection refers to the ‘examination of an electrical installation using all the senses as appropriate’ (NOT using instruments).

- the Testing refers to ‘ascertaining values by means of appropriate measuring instruments’.

- the Commissioning includes the issuing of either an installation certificate (EIC or MEIWC).

Step 1

- Whilst undertaking Inspecting and Testing of electrical Installations there are legal duties to establish and maintain a safe working environment.

What document should be completed by the employer to take in to account any hazards that might be present e.g., that there is safe access and egress around the work area, that you have eliminated or controlled all work area hazards to property, personnel and livestock, etc.

| References: - Text Book B Chapter ELTK 06 pages 76 - 77 | - YouTube videos: Guide to Risk Assessment |
| --- | --- |

- Which Statutory Document made under the Health Safety at Work Act, applies to terminating and connecting electrical systems?

| References: - Text Book B Chapter ELTK 06 page 77 | - YouTube videos: Statutory_Non-statutory 08:00 – 08:55 |
| --- | --- |

- Which Non-statutory document contains regulations that apply to the selection and erection of wiring systems, including their termination and connections?

| References: - Text Book B Chapter ELTK 06 page 77 | - YouTube videos: Statutory_Non-statutory 08:00 – 08:55 |
| --- | --- |

Step 1 continued

- What safety procedure should be followed prior to carrying out the inspection and testing of electrical installations?

| References: Text Book B Chapter ELTK 06 page 78 | - YouTube videos: Health & Safety 01:45 |
| --- | --- |

- What are the implications of not carrying out safe isolation prior to carrying out the inspection and testing of an electrical installation?

| References: Text Book B Chapter ELTK 06 page 76 | - YouTube videos: Health & Safety 01:13 |
| --- | --- |

Step 2

- What does the term Initial Verification refer to?

| References: Text Book B Chapter ELTK 06 page 78 | - YouTube videos: Initial Verification 01:35 |
| --- | --- |

- What section of the IET Wiring Regulations provides guidance on INITIAL VERTIFACTION?

| Part: |  |
| --- | --- |
| Chapter: |  |
| References: - Text Book B Chapter ELTK 06 page 78 | - YouTube videos: BS7671:2018 00:00 – 01:20 |

- When should the Initial Verification Inspection be carried out?

| References: Text Book B Chapter ELTK 06 page 79 | - YouTube videos: BS7671 Part 6 01:25 – 01:50 |
| --- | --- |

Step 2 continued

- What does the term PERIODIC INSPECTION refer to?

| References: - Text Book B Chapter ELTK 06 pages 78 - 79 | - YouTube videos: BS7671 Part 6 11:25 – 13:25 |
| --- | --- |

- What section of the IET Wiring Regulations provides guidance on PERIODIC INSPECTION?

| Part: |  |
| --- | --- |
| Chapter: |  |
| References: - Text Book B Chapter ELTK 06 page 78 | - YouTube videos: BS7671:2018 00:30 – 06:34 |

- Explain reasons for carrying out inspection and testing during Initial Verification.

| References: - Text Book B Chapter ELTK 06 page 99 | - YouTube videos: BS7671 Chapter 64 5:10 – 6:50 |
| --- | --- |

- What information would the inspector require to conduct the Initial Verification of an electrical installation?

| Refer to | Information |  |
| --- | --- | --- |
| BS7671:2018 Section 132 |  |  |
| BS7671:2018 Section 311 |  |  |
| BS7671:2018 Section 312 |  |  |
| BS7671:2018 Section 313 |  |  |
| BS7671:2018 Section 511 |  |  |
| References: - Text Book B Chapter ELTK 06 pages 91 - 93 |  | - YouTube videos: BS7671 Part 5 2:15 – 3:15 |

Step 2 continued

- What documents would be completed and issued following INITIAL VERIFICATION?

| References: - Text Book B Chapter ELTK 06 pages 146 - 157 | - YouTube videos: BS7671 Chapter 64 08:55 – 09:45 |
| --- | --- |

- What documents would be completed and issued following PERIODIC INSPECTION?

| References: - Text Book B Chapter ELTK 06 pages 146 - 157 | - YouTube videos: BS7671 Chapter 64 08:55 – 09:45 |
| --- | --- |

Step 3

- INSPECTION refers to the use of the appropriate human senses during the examination of electrical installations? State which senses would be used and give an example of what for.

| Human sense | Example of use |  |
| --- | --- | --- |
| References: - Text Book B Chapter ELTK 06 pages 83- 87 |  | - YouTube videos: Inspection requirements 07:50 – 09:35 |

Step 3 continued

- What should the Inspector do if an item inspected is found to be unsatisfactory?

| References: - Text Book B Chapter ELTK 06 page 123 | - YouTube videos: Inspection requirements 09:50 – 11:45 |
| --- | --- |

- What IP codes should the inspector consider to be the minimum for an indoor enclosure such as a wall surface mounted consumer unit?

| References: - Text Book B Chapter ELTK 06 page 108 | - YouTube videos: Inspection requirements 11:45 – 12:20 |
| --- | --- |

- What Part of BS7671 deals with additional requirements for SPECIAL INSTALLATIONS OR LOCATIONS , including Bathrooms?

| References: - Text Book B Chapter ELTK 06 page 83 | - YouTube videos: Inspection requirements 12:20 – 12:45 |
| --- | --- |

- What are the main differences when completing the Schedule of Inspection for new installation work compared to completing the Schedule of Inspection for Periodic Inspection?

| References: - IET Model Forms – Schedule of Inspections | - YouTube videos: Inspection requirements 13:00 – 19:00 |
| --- | --- |

Step 4

- What checks would be carried out on a Multi-function installation tester prior to carrying out the ‘dead’ tests on a ring final circuit feeding 13A switched socket outlets?

| Checks to be made |  | Regarding |
| --- | --- | --- |
|  |  | Instrument on-going accuracy Setting up a tester 00:00 – 01:50 |
|  |  | Instrument power supply Setting up a tester 02:50 – 03:10 |
|  |  | Instrument leads/ accessories Setting up a tester 03:55 – 06:10 |
|  |  | Instrument socket adaptor Setting up a tester 06:11 – 08:00 |
|  |  | Instrument 500V test facility Setting up a tester 09:28 – 10:48 |
| References: Text Book B Chapter ELTK 06 page 77 BS7671:2018 Chapter 64 page 231 | - YouTube videos: Setting up a tester 00:00 – 11:10 |  |

- What are the four ‘dead’ tests that would be carried out on a newly installed standard domestic ring final circuit feeding 13A switched socket outlets? (TN-C-S Earthing arrangement)

| Test |  | Regulation |
| --- | --- | --- |
|  |  | 643.2.1 (i) |
|  |  | 643.2.1 (ii) |
|  |  | 643.3 |
|  |  | 643.6 |
| References: Text Book B Chapter ELTK 06 page 100 BS7671:2018 Chapter 64 pages 232 - 234 | - YouTube videos: Order of testing 01:00 – 03:45 |  |

Step 4 continued

- State three key requirements of HSE Guidance Note GS38 with respect to ‘Live’ Testing.

| GS38 requirements |  | Regarding |
| --- | --- | --- |
|  |  | Test probe tips |
|  |  | Test probe shape |
|  |  | Probe fault protection |
|  |  | Test lead identification |
| References: Text Book B Chapter ELTK 06 page 100 BS7671:2018 Chapter 64 pages 232 - 234 | - YouTube videos: GS38 |  |

- What are the three ‘live’ tests that would be carried out on a newly installed standard domestic ring final circuit feeding 13A switched socket outlets? (TN-C-S Earthing arrangement)

| Test |  | Regulation |
| --- | --- | --- |
|  |  | 643.7.3 |
|  |  | 643.8 |
|  |  | 643.10 |
| References: Text Book B Chapter ELTK 06 page 77 HSE GS38 pages 4 - 6 | - YouTube videos: Order of testing 03:46 – 08:00 |  |

- What should the Inspector do if a newly installed item tested is found to be unsatisfactory?

| References: - Text Book B Chapter ELTK 06 page 123 | - YouTube videos: Inspection requirements 09:50 – 11:45 |
| --- | --- |

Step 4 continued

- For each of the following state the purpose of the ‘dead’ test and implications if not carried out:

| Test | Purpose of the test |  | Implication(s) if not carried out |
| --- | --- | --- | --- |
| Continuity of Main Bonding Conductors |  |  |  |
| Continuity of Radial circuit Protective Conductors |  |  |  |
| Continuity of Ring circuit Protective Conductors |  |  |  |
| Insulation Resistance |  |  |  |
| Polarity |  |  |  |
| References: - Text Book B Chapter ELTK 06 page 100 - 111 |  | - YouTube videos: Order of testing 01:00 – 03:25 |  |

- For each of the following state the purpose of the ‘live’ test and implications if not carried out:

| Test | Purpose of test |  | Implication(s) if not carried out |
| --- | --- | --- | --- |
| External Earth Fault Loop Impedance (Ze) |  |  |  |
| Circuit Earth Fault Loop Impedance (Zs) |  |  |  |
| Prospective Fault Current at the origin (PFC) |  |  |  |
| Phase sequence |  |  |  |
| RCD/ RCBO operation |  |  |  |
| References: - Text Book B Chapter ELTK 06 page 114 - 122 |  | - YouTube videos: Order of testing 04:20 – 06:06 |  |

Step 4 continued

- Describe how each of the following three factors can affect the value of resistance measured during continuity testing:

| Factor | Effect on conductor resistance value |  |
| --- | --- | --- |
| Cable Length (m) |  |  |
| Cable CSA (mm2) |  |  |
| Ambient Temperature (OC) |  |  |
| References: Text Book B Chapter ELTK 06 page 116 |  | - YouTube videos: Resistance value 00:35 – 04:25 |

- Explain where you could source information to verify the following test measurement results:

| Test measurement result | Source of information to assist in verification of test result |  |
| --- | --- | --- |
| 0.08Ω measured during continuity testing of 10mm2 main bonding conductor |  |  |
| 65MΩ measured during insulation resistance testing of 3-phase M.I. cable circuit |  |  |
| 1.05Ω measured during the Loop Impedance testing of a radial circuit protected by a B32 60898 circuit breaker |  |  |
| 42mS trip time measured for a 100mA RCD used for fault protection |  |  |
| References: Text Book B Chapter ELTK 06 pages 100 - 116 |  | - IET On-Site Guide pages 11, 99, 131, and 196 |

- Ze and Ipf can be ascertained by measurement or by enquiry.     Explain how Ze and Ipf  would be determined by enquiry, and the likely declared values for a typical new build single-phase supply.

| Supply parameter | Declared values | Determined by: |  |
| --- | --- | --- | --- |
| Ze |  |  |  |
| Ipf |  |  |  |
| References: - Text Book B Chapter ELTK 06 pages 119, 148, & 156 |  |  | - IET On-Site Guide pages 11 & 99 |

Step 4 continued

- What precautions need to be taken prior to Insulation Resistance testing in respect of:

| Factor | Precaution to be taken |  |
| --- | --- | --- |
| devices installed that are likely to influence the test measurement |  |  |
| devices installed that are likely to be damaged by the test and cannot be readily disconnected |  |  |
| References: - Text Book B Chapter ELTK 06 page 106 |  | - YouTube videos: Insulation Resistance Test 00:45 – 01:10 |

- What Test Voltage and Minimum Insulation Resistance apply to the following:

| Circuit | Test Voltage |  | Minimum Insulation Resistance |
| --- | --- | --- | --- |
| 12v a.c. extractor fan (SELV) |  |  |  |
| 230v a.c. shower circuit |  |  |  |
| 400v a.c. 3-phase motor |  |  |  |
| References: - Text Book B Chapter ELTK 06 page 107 |  | - YouTube videos: Insulation Resistance Test 01:25 – 03:40 |  |

- What happens to the Insulation Resistance of a circuit when the cable length is increased?

| Effect on existing Insulation Resistance value |  |
| --- | --- |
| References: - Text Book B Chapter ELTK 06 page 125 | - YouTube videos: Insulation Resistance Failure |

- What happens to the Insulation Resistance of a circuit when additional circuits are added to an installation?

| Effect on existing Insulation Resistance value |  |
| --- | --- |
| References: - Text Book B Chapter ELTK 06 page 125 | - YouTube videos: Insulation Resistance Failure |

Step 4 continued

Regulation 643.7 requires verification of the measures to protection by Automatic Disconnection of Supply (ADS).

- Explain how the following formula could be used to ascertain EFLI   Zs = ZE + (R1 + R2):

| References: - Text Book B Chapter ELTK 06 page 126 | - YouTube videos: Total Earth Fault Loop Impedance |
| --- | --- |

- Explain how the value of EFLI (Zs) can be used to ensure the effectiveness of ADS for a circuit protected by a B32 circuit breaker to BSEN 60898.

| References: - Text Book B Chapter ELTK 06 page 126 | - YouTube videos: EFLI 80% correction factor 00:00 – 05:05 |
| --- | --- |

- Following Initial Verification, who recommends the date to the first Periodic Inspection?

| References: - BS7671:2018 Regulation 134.2.2 page 23 |  |
| --- | --- |

SEE NEXT PAGE FOR TESTING VIDEO LINKS

Step 5

- The following table contains the typical tests that would be carried out within a dwelling.

| The following YouTube video links depict tests carried out on low voltage circuits (UO - 230v) in a training environment and are a demonstration of what would be required during an assessment. |  |  |
| --- | --- | --- |
| Test type | Regulation | YouTube video link |
| Main bonding conductor (R2 method) | 643.2.1 (i) | QR code 1 - Main bonding |
| Continuity of Radial Circuit (R1+R2 method) | 643.2.1 (i) | QR code 3 - R1 + R2 method |
| Continuity of Ring Final Circuit | 643.2.1 (ii) | QR code 5 - Ring Circuit Continuity |
| Insulation Resistance | 643.3 | QR code 6 - Single phase Insulation Resistance |
| Polarity | 643.6 | QR code 8 - Polarity as part of R1 + R2 |
| Earth Fault Loop Impedance (Ze) | 643.7.3 | QR code 10 - Ze for a TT system |
| Earth Fault Loop Impedance (Zs) | 643.7.3 | QR code 11 - Zs of lighting circuit |
| Prospective Fault Current (Ipf) | 643.7.3.201 | QR code 12 - Prospective Fault Current |
| RCD for additional Protection | 643.8 | QR code 13 - RCD testing |

- The following table contains additional tests that may need to be carried out where relevant.

| The following YouTube video links depict tests carried out on low voltage circuits (UO - 230v) in a training environment and are a demonstration of what would be required during an assessment. |  |  |
| --- | --- | --- |
| Test type | Regulation | YouTube video link |
| Supplementary bonding conductor | 643.2.1 (i) | QR code 2 - Supplementary bonding |
| Three-phase Continuity (R1+R2 method) | 643.2.1 (i) | QR code 4 - 3-phase R1 + R2 method |
| Three-phase Insulation Resistance | 643.3 | QR code 7 - 3-phase Insulation Resistance |
| Earth Electrode | 643.7.2 | QR code 9 - Earth Electrode |